## Slide 1: Spill Prevention, Control, and Countermeasures (SPCC) and Facility Response Plan (FRP) Rules Overview
Module 3
Angelica Villa 3/24/2026
Notes: Thank you, Steve, for walking us through the regulatory framework. Now we are going focus on how these requirements apply specifically to facilities that need to have a SPCC plan an approved FRP.
Let me start we a quick question. If a worst-case spill happened at your facility today, do you know exactly what EPA expects you to have in place to respond? Pause…..THAT IS WHY EPA CONDUCTS WORKSHOPS LIKE THIS.

## Slide 2: Objective
By the end of the presentation, attendees should be able to:
  Understand the SPCC/FRP Rules
  Enhance their ability to effectively utilize their Facility Response Plan (FRP) and Emergency Response Action Plan (ERAP) during a GIUE or emergency oil spill response.
FRP rule (40 CFR 112.20–112.21)
Notes: By the end of the presentation, attendees should be able to:
  Understand the SPCC/FRP Rules
  Enhance their ability to effectively utilize their Facility Response Plan (FRP) and Emergency Response Action Plan (ERAP) during a GUIE or emergency oil spill response.

## Slide 3: Topics
SPCC
  Applicability
  Terms and Definitions
  General Requirement
  Preparation, Reviews and amendments
FRP
  Applicability
  Substantial Harm Criteria/Sig-Sub Harm Criteria
  Required Submissions
  General Requirements
Notes: We will discuss the SPCC and FRP rules—applicability, key terms and definitions, general requirements, and plan preparation, review, and amendment.
We will also cover FRP‑specific items: the substantial‑harm criteria and the significant‑and‑substantial harm designation.

## Slide 4: Oil Discharges Occur!
Notes: Oil discharge happened!
In 2022, a colleague and I were conducting FRP Compliance Inspections, when we arrived at this facility, we couldn’t believe what we saw. Oil everywhere.
We learned that the oil discharge had occurred earlier due to pump failure.
Fortunately, the spill was discovered immediately and THE FACILITY had an excellent emergency response plan.
In addition, the facility had not only secondary containment but tertiary one.
The facility was at less than 1000 ft from WOTUS. Had the oil reached the water, the cleanup would have been very expensive.
THART IS WHY WE HAVE REGULATIONS IN PLACE TO PREVENT ENVIRONMENTAL DISASTER AND TO SAVE YOUR COMPANY MONEY.

## Slide 5: Spill Prevention Control and Countermeasures 112.1(b)
SPCC
§40 CFR 112.1
Notes: First, we’ll discuss the SPCC rule. Then we’ll discuss the FRP rule

## Slide 6: SPCC General applicability
Non-transportation-related facility (Appendix A)
Reasonable expectation of oil discharge that could impact WOTUS or adjoining shorelines
Harmful Quantities
Aggregate storage capacities
  AST 1,320 gallons (~32bbl)
  UST 42,000 gallons (1,000bbl)
§40 CFR 112.1
Cause a Sheen
Violates Applicable Water Quality Standards
Notes: 6. Applicability to the rule is described in 40 CFR 112.1 which states, ‘The rule applies to the owners and operators of non-transportation-related onshore and offshore facilities that, because of their location could reasonably be expected to discharge oil into navigable waters of the United States or adjoining shorelines in quantities that may be harmful, as described in part 110 of this chapter.
AND to facilities that have more than 1,320 gallons of storage capacity in aboveground oil tanks or more than 42,000 gallons of underground oil storage capacity, and a discharge could reasonably be expected to reach navigable waters or adjoining shorelines, then the SPCC rule applies.
How do you know if the quantities may be harmful?
According to section 10.3, Quantities that may be Harmful include discharges of oil that
(a) Violate applicable water quality standards; or
(b) Cause a sheen upon or discoloration of the surface of the water

## Slide 7: 40 CFR 112.1(b) General SPCC Rule Applicability- Engage on
Drilling
Gathering
Processing
Producing
Storing
Drilling
Producing
Gathering
Storing
Processing
Refining
Transferring
Distributing
Consuming oil and oil products
Refining
Transferring
Using
Notes: 7. In addition, the regulation further explains that general SPCC rule applies to any owner or operator of a non‑transportation‑related, onshore or offshore facility engaged in: Drilling/Producing/Gathering/Storing/Processing/Refining/Transferring/Distributing/Consuming oil products which due to its location, could reasonably be expected to discharge oil in quantities that may be harmful

## Slide 8: Reasonable Expectation of an Oil Discharge
Geography and location relative to WOTUS
Determine if any conveyance exists
Volume of oil discharge/flow path
Notes: 8. Reasonable Expectation of an Oil Discharge
How do you determine whether there is a reasonable expectation of discharging oil ino navigable waters or adjoining shorelines from your facility?
Consider your facility’s location and slope in relationship to nearby navigable waters (streams, creeks, rivers, lakes, wetlands).
Identify drainage systems—such as storm sewers, culverts—that could carry oil off site to those waters.
Estimate the volume of oil that could be spilled in an incident and how that oil might flow from your facility.

## Slide 9: Reasonable Expectation of an Oil Discharge
Soil and geologic conditions
Precipitation runoff
Quantity and oil stored
Past discharges
Notes: 9. Reasonable Expectation of an Oil Discharge
Look at the soil conditions or geologic features that might affect the flow toward waterways.
Also consider whether stormwater runoff could transport oil into navigable waters or adjoining shoreline? For example: At an asphalt facility, ask yourself, “If a WCD occurs during a rainstorm outside containment, could stormwater runoff carry oil to WOTUS?”
You must also consider discharge history and how that may impact the probability of future discharge.
You may not take into account manmade features, such as dikes, equipment, or other structures that might prevent, or restrain the flow of oil.
Assume these manmade features are not present when making your determination.
If you consider these applicable factors and determine a spill can reasonably flow to a waterway, then you must comply with the SPCC rule

## Slide 10: 40 CFR 112.2 “Oil” Definition
Fats, Oils, or Grease of:
Vegetable Oil:
Other oils and greases, including petroleum, fuel oil, sludge, synthetic oils, mineral oils, oil refuse, or oil mixed with wastes other than dredged spoil
Animal
Fish
Marine Mammal Origin
Whale
Seeds
Nuts
Kernels

## Slide 11: What is a Discharge
§110 “sheen rule” §112.2
40 CFR 112.2 “Discharge”
includes, but is not limited to any spilling, leaking, pumping, pouring, emitting, emptying, or dumping of any amount of oil no matter where it occurs
Notes: §112.2 SPCC
any spilling, leaking, pumping, pouring, emitting, emptying, or dumping of any amount of oil no matter where it occurs
§112.1(b)/§110
causes a sheen or discoloration, sludge or emulsion to be deposited, or violation of water quality standard

## Slide 12: What is a Discharge?
§110 “sheen rule” §112.2
40 CFR 110.3:​
Cause a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or
Cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines or
Violates water quality standard
Notes: According to 40 CFR 10.3: Includes a discharge of oil that causes…
Water quality standards established under CWA

## Slide 13: Facility Boundaries
Things to consider:
Ownership, management, and operation
Similar functions, characteristics, and types of activities
Shared drainage pathway
Aggregation
§112.2
Notes: The boundary of a “facility” depends on site-specific circumstances. Factors that may be considered relevant in delineating the boundaries of a facility may include, but are not limited to:
Ownership, management, and operation of the buildings, structures, equipment, installations, pipes, or pipelines on the site
Similar functions, operational characteristics, and types of activities occurring at the site;
Proximity, or Shared drainage pathways (e.g., same receiving water bodies).
EXAMPLE OF DIFFERENT OPERATIONAL CHARACTERISTICS: A site with three distinct operations was split into three facilities; two were not subject to FRP, and one still required a plan
EXAMPLE OF DIFERENT DIFFERENT DRAINAGE PATHWAYS: A couple of years ago, we inspected a site with three tank battery areas miles apart, each draining to a different receiving water. Based on our advice to reconsider the facility boundaries, the operator split the site into three separate facilities; the resulting facilities were legally not subject to the FRP rule.

## Slide 14: Separation
Notes: A facility may or may not be subject to the SPCC and FRP rule requirements depending on site-specifics characteristics, but, once the facility determine the facility boundaries for SPCC applicability, then the same boundaries apply for determining applicability of the FRP rule requirements.
You can’t draw boundaries just to avoid the FRP rule.

## Slide 15: General Requirements for SPCC Plans: 40 CFR 112.7
Describe physical layout with diagram
  Location and contents of each fixed oil container
  Storage areas for mobile/portable containers
  All transfer areas and connecting piping
  Exempt completely buried USTs exempt under 40 CFR 112.1(d)(4) labeled “exempt”
  Permanently closed containers
  Breakout tanks
Notes: Under 40 CFR 112.7, your SPCC Plan must describe the facility’s physical layout and include a diagram that shows every fixed oil container, portable storage area, transfer area, and connecting piping you control.
The diagram must also identify and mark EXEMP
Any completely buried USTs
Any permanently closed containers
Breakout tanks

## Slide 16: General Requirements for SPCC Plans: 40 CFR 112.7
  Discharge Prevention Measures
  Discharge or Drainage Controls
  Countermeasures
  Disposal of recovered oil
  Emergency contact list
Notes: Your Plan must also describe:
Discharge prevention measures such as secondary containment and good engineering practices
Drainage controls. For example: At an asphalt facility, ask yourself, “If a WCD occurs during a rainstorm outside containment, could stormwater runoff carry oil to WOTUS?”
Countermeasures for discharge discovery, response, and cleanup.
How recovered oil will be disposed of in accordance with applicable legal requirements.
Emergency contact list that includes:
    The facility emergency response coordinator,
    contractors
    NRC
    Appropriate Federal, State, Tribal, and local agencies to be notified

## Slide 17: Exempt oil containers’ capacities: 40 CFR 112.1(d)
Capacity of bulk storage container used primarily to power the movement of a motor vehicle
Capacity of hot-mix asphalt (HMA) or any HMA container
Capacity of single-family residential heating oil
Capacity of pesticide application equipment and related mix containers
Capacity of milk and milk product containers
Capacity of containers used exclusively for wastewater treatment
Notes: 17. Do not count the following toward your total aboveground storage capacity:
Motive power containers (bulk storage container used primarily to power the movement of a motor vehicle)
Hot-mix asphalt (HMA) or any HMA containers
Single-family residential heating oil containers
Pesticide application equipment and related mix containers
Milk and milk product containers and associated piping and appurtenances
Containers used exclusively for wastewater treatment

## Slide 18: Discharge or drainage controls
40 CFR 112.8
Specific (Sized) Secondary Containment
Bulk containers: capacity of largest single container + freeboard
Loading racks: maximum capacity of any single compartment
40 CFR 112.7(c)
General Secondary Containment
Requirements:
  Contain oil
  Address the typical failure mode
  Address the most likely quantity
Can be Passive or Active
§112.7(a)(3)(iii))
Notes: 18. We used general/sized secondary containment for discharge or drainage controls:
The General Secondary Containment Must be able to:
  Contain oil
  Address the typical failure mode
  Address the most likely quantity
Can be Passive or Active
AND The sized secondary containment requirements are intended to address a major container failure and are required for bulk storage containers;
For Bulk containers, the Secongary containment must have the capacity of the largest single container plus freeboard.
For loading racks, containment must hold the maximum capacity of any single compartment.

## Slide 19: 40 CFR 112.8 Provide appropriate containment and/or diversionary structures or equipment to prevent a discharge
Sized Secondary Containment for Bulk Containers
Notes: Here we have examples of Sized secondary containment.
Is this retaining walls sufficiently impervious to contain oil?

## Slide 20
General or Sized Secondary Containment?
Spill kit
Notes: 19. Are these examples active of passive GENERAL secondary containment?
If someone must take action to put a containment measure in place, it is active.
If it is always in place, it is passive. berms/curbing/Double-walled tanks, etc.

## Slide 21: Do you count these containers towards your aggregate storage volume?
Do you need to include every drum in your inventory list?
Should the facility include these mobile/portable containers in their SPCC plan?
Notes: Do you count these containers towards your aggregate storage volume?
Yes. You should count portable containers that are 55 gallons or larger. You don’t need to list every individual drum; instead, you may provide an estimate of the number of portable containers, the types of oil, and their anticipated storage capacities.

## Slide 22: Oil-Filled Operational Equipment
Oil used for/in the operation of that equipment
Is not considered a bulk storage container
General containment requirement with exceptions
40 CFR 112.7(k)
Notes: 22. Oil-filled operational equipment” is defined under §112.2 as equipment that includes an oil storage container in which the oil is present solely to support the function of the apparatus or the device.
Oil-filled operational equipment is not considered a bulk storage container: ex: Transformers, generators, etc.
So, it only requires General containment requirement.
If, in the past 3 years, there has been no single 1,000‑gallon spill and no two 42‑gallon spills within any 12‑month period, you may use the alternative to general secondary containment. In that case, implement:
An oil spill contingency plan
Documented inspection/monitoring to detect failures or discharges
A written commitment of resources to promptly control and remove discharged oil

## Slide 23: Transfers
Loading/Unloading Areas
General containment
Loading/Unloading Racks 112.8
Specific (sized) containment
Loading/unloading arm
Visual inspections
Warning signs, wheel chock, interlock system
Notes: 23. What type of secondary containment is needed for
Loading/Unloading Areas: Must have a General secondary containment
Loading/unloading rack has Loading/unloading arm and Must have a Sized, passive secondary containment:
The operator must conduct:
Visual inspections and the area must include
Warning signs, wheel chock, interlock system

## Slide 24: SPCC Plan preparation, reviews and amendments
Must prepare in writing and implement a SPCC Plan (§ 112.7)
New Operations 112.3(b)
  six months to prepare and implement
Good engineering practices
Full approval of management
Notes: 24. If you are the owner or operator of a facility subject to this part, you must prepare in writing and implement a Spill Prevention Control and Countermeasure Plan in accordance with § 112.7 and any other applicable section of this part.
For new facilities just starting operations or existing facilities that because of modifications are now required to develop an SPCC
You have 6-months to develop and implement a plan from the date of start-up.
You must prepare a Plan in accordance with good engineering practices
The Plan must have the full approval of management at a level of authority to commit the necessary resources to fully implement the Plan
You are not required to submit your plan initially. EPA may ask for your plan related to inspection activities or in the event of a reportable discharge. This is different than the FRP requirements.

## Slide 25: SPCC Plan preparation, reviews and amendments - Continued
A licensed Professional Engineer must review and certify a Plan
Have a Professional Engineer certify any technical amendments
Review and evaluation of the SPCC Plan at least once every five years
Notes: Does the SPCC need to be certified by a PE?
Yes, a licensed Professional Engineer must review and certify the plan a AND any technical amendments
A complete a review and evaluation of the SPCC Plan at least once every five years from the date your facility becomes subject to this part

## Slide 26: Reviews and Amendments
By Regional Administrator
Discharges
  Any single > 1,000 gal to WOTUS
  Two > 42 gal in 12-month period to WOTUS
30 days to amend, 6 months to implement
By Owner/Operator
Material changes
Every 5 years
6 months to amend, 6 months to implement
Notes: Two types of amendments can occur:
Amendment Required by Regional Administrator and By Owner or Operator
Amendment by the RA following a single discharge of more than 1,000 gallons or more than two discharges of 42 gallons into WOTUS in 12-month period.
Timing: 30 days to amend, 6 months to implement
Amendment by the Operator
Required after any material change and at each five‑year review.
Timing: 6 months to amend; 6 months to implement.
Any amendments must PE-certified.

## Slide 27: Inspections and Tests
Facilities must:
Conduct inspections and tests in accordance with written procedures
And appropriate industry standards
  Qualifications of personnel
  Frequency and type
Sign and maintain all records with plan for 3 years
  Available at facility
112.7(e)
Notes: Facilities must:
Conduct inspections and tests according to the SPCC plan and applicable industry standards.
Use qualified personnel and follow the frequency and methods specified in the SPCC Plan.
Keep inspection test records signed and dated for at least 3 years.
Common deficiency: Missing signatures or incomplete records.
Available at facility

## Slide 28
Inspect the container's supports and foundations for signs of deterioration, or discharges,
Also, for signs of accumulation of oil inside diked areas.
Keep certified inspector comparison records for the lifetime of the tank.
Notes: Keep certified inspector comparison records for the lifetime of the tank.

## Slide 29: Ashland Oil Spill
1 million gallons of diesel discharged into a storm sewer -> WOTUS
Failed to conduct integrity testing
$2.25 million in penalties and $18 million in cleanup costs
40 CFR 112.7(i)
Notes: Reason for failure: B/C Failed to conduct integrity testing.
Ashland Co. later took full responsibility for the incident, accepting that they did violate industry standards when reconstructing the tank
Ashland Oil Company Inc. (currently known as Ashland Inc.) owned a facility near the Monongahela River in Jefferson, PA (now Jefferson Hills). On January 2, 1988, a four-million gallon tank was used for the first time after being dismantled (from an Ohio location) and rebuilt in Pennsylvania. It was this tank, holding approximately 3.5 million gallons of diesel oil, that failed and collapsed, dumping nearly 1 million gallons of the oil into a storm sewer that led to the Monongahela River.[2] At 4:58pm, a worker checked the tank levels and verified the tank was almost full. At 5:02, when the worker was walking away from the tank, he heard a loud boom and turned to find the roof of the tank collapsed.[3] Ashland Co. later took full responsibility for the incident, accepting that they did violate industry standards when reconstructing the tank.[4]
A team of researchers ultimately discovered that a dime-sized flaw on the 45-year-old tank contributed to the rupture. The flaw, which consisted of a small, rusting cavity about 0.125 in. deep was caused by a torch and was in the steel before reassembly. A combination of factors aggravated the flaw and caused the tank to split. The tank was assembled in Cleveland in 1940 and rebuilt in 1985. The original welds and those used during the reassembly made the tank’s steel walls more brittle. Other contributing factors were the relative weakness of the World War II steel, pressure from the diesel fuel, and cold weather.[5]
From the Monongahela River, the oil made its way down into the Ohio River, contaminating the drinking water for about 1 million people throughout Ohio, West Virginia, and Pennsylvania.[1] About 23,000 residents of Pittsburgh were without water for a week.[4] About 1,200 residents of Jefferson Borough were asked to evacuate due to fear of an explosion in the area from a gasoline leak.[2] Water shortages occurred for areas as far as 200 miles down river. This oil spill was one of the largest inland oil spills at the time of occurrence. The U.S. Government estimated the cost of damages were between $10 and $15 million.[6]
Wildlife in the region were harmed by the oil as well. Fish and mussels were affected as well as 2,000-4,000 water fowl were killed in the incident.[3]
The first Federal government agents on scene were the United States Coast Guard, and the Environmental Protection Agency acted as on scene coordinators throughout the cleanup process.[3] Multiple obstacles were faced throughout the cleanup efforts. First, major water shortages down river placed potable water in high demand. Also, cold temperatures caused freezing and extreme conditions throughout the river, hindering the cleanup process. Lastly, the river itself had few access points, making it difficult to bring in heavy equipment for cleanup in certain parts of the river. Out of the approximate 1 million gallons spilled, about 200,000 gallons were recovered in the process.

## Slide 30: Personnel Training
    Operation and maintenance of equipment
    Response procedures
    General facility operations
    Contents of the facility SPCC Plan
    Applicable pollution laws and regulations
40 CFR 112.7(f) (1)
Notes:   At a minimum, train your oil-handling personnel in:
    Operation and maintenance of oil spill response equipment
    Response procedures
    General facility operations
    Contents of the facility SPCC Plan
    Applicable pollution laws and regulations
Training of oil-handling personnel is required for facilities subject to the SPCC rule.
Records aren’t required, but they should be kept to document that training has taken place. Sign-in sheets work well.
(f) Personnel, training, and discharge prevention procedures.
(1) At a minimum, train your oil-handling personnel in the operation and maintenance of equipment to prevent discharges; discharge procedure protocols; applicable pollution control laws, rules, and regulations; general facility operations; and, the contents of the facility SPCC Plan.
(2) Designate a person at each applicable facility who is accountable for discharge prevention and who reports to facility management.
(3) Schedule and conduct discharge prevention briefings for your oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan for that facility. Such briefings must highlight and describe known discharges as described in § 112.1(b) or failures, malfunctioning components, and any recently developed precautionary measures.

## Slide 31: Discharge Prevention Briefings
Conduct at least annually
All oil-handling personnel
SPCC review
Discuss
  Discharges and failures
  Malfunctioning components
  Any recently developed precautionary measures
40 CFR 112.7(f)(3)
Notes: The SPCC Plan must include:
A description of annual discharge‑prevention briefings for all oil‑handling personnel.
An SPCC review covering
  recent discharges and failures,
  malfunctioning components,
  and newly developed precautionary measures.

## Slide 32
112.8 Onshore Facilities (bulk)
Facility Drainage
Bulk Storage Containers
112.9 Onshore Production Facilities
Facility Drainage
Bulk Storage Containers
112.10 Onshore Drilling and Workover
Discharge prevention
112.12 AFVO
Facility transfer operations, pumping, and facility process
Flow-through process vessels
Produced water containers
Facility transfer operations
Facility Drainage
Bulk storage containers
Bulk storage container inspections
Facility transfer operations, pumping, and facility process.
Facility Specific Requirements
See Inspection Records Review List
Notes: Each facility type has its own facility‑specific requirements for inspections, testing, training, and drills/exercises (see the Inspection Records Review List):
Onshore facilities (excluding production) – petroleum oils
Onshore oil production facilities
Onshore oil drilling and workover facilities
Onshore facilities handling animal fats and vegetable oils (AFVO)

## Slide 33: Applicability-Facility Response Plan 40 CFR §112.20
Facility Response Plan
See Attachment C-II Certification of the Applicability of Substantial Harm Criteria
Notes: Facilities who meet the substantial harm criteria as defined 40 CFR 112.20 are required to prepare a Facility Response Plan (FRP).
Appendix C to part 112 - Substantial Harm Criteria provides guidance for determining FRP applicability.

## Slide 34: FRP Rule Purpose and Applicability
“could reasonably be expected to cause substantial harm to the environment by discharging oil into or on the navigable waters or adjoining shorelines”
The purpose of the FRP rule is to ensure facilities have an approved FRP to respond to the Worst-case discharge
Notes: Facilities:
That could reasonably be expected to cause substantial harm to the environment by discharging oil into or on the navigable waters or adjoining shorelines
Must plan for and respond to a worst-case discharge

## Slide 35: Substantial Harm
42,000 Gallons of Storage
Transfers over water to vessels
1 Million Gallons of Storage
Inadequate secondary containment
Shutdown public drinking water intake
Injury to fish and wildlife and sensitive environments
Discharge ≥ 10,000 gallons
Notes: 42,000 Gallons of Storage AND Transfers over water to vessels
1 Million Gallons of Storage AND
Inadequate secondary containment
Injury to fish and wildlife and sensitive environments
Shutdown public drinking water intake
Discharge ≥ 10,000 gallons

## Slide 36: Substantial Harm Criteria Exercise
  Using the blank C-II form fill out the necessary information specific to your facility
Notes: Who Makes the Substantial‑Harm Criteria Determination?
40 CFR Appendix C to Part 112 - FRPs are required to include the Substantial Harm Criteria form. This form details why the FRP rule applies to the facility, while also helping to determining whether the facility is considered capable of substantial harm or significant and substantial harm.
Facilities who fall in the Significant and Substantial Harm category are required to seek EPA approval for their plans. Ultimately, whether a facility falls in the significant harm or significant and substantial harm category is at the Regional Administrator’s discretion.

## Slide 37: Substantial Harm
Regional Administrator Determination
Type of operation
Oil Storage Capacity
Lack of Secondary containment
Proximity to F&W and sensitive environments
Proximity Drinking water intakes
Spill history
Other site-specific and environmental factors
Notes: 40 CFR 112.20(f)(2)(i) To determine whether a facility could, because of its location, reasonably be expected to cause substantial harm to the environment by discharging oil into or on the navigable waters or adjoining shorelines pursuant to paragraph (b) of this section, the Regional Administrator shall consider the following:
(A) Type of transfer operation;
(B) Oil storage capacity;
(C) Lack of secondary containment;
(D) Proximity to fish and wildlife and sensitive environments and other areas determined by the Regional Administrator to possess ecological value;
(E) Proximity to drinking water intakes;
(F) Spill history; and
(G) Other site-specific characteristics and environmental factors that the Regional Administrator determines to be relevant to protecting the environment from harm by discharges of oil into or on navigable waters or adjoining shorelines.

## Slide 38: Significant & Substantial Harm
Based on the following factors:
  Past discharges
  Proximity to waters
  Age of storage tanks
  Vulnerable Receptors will be impacted prior to arrival and deployment of response assets
  Other facility-specific and Region-specific information
EPA will issue notification of determination
At a minimum review, every 5 years
Notes: To determine whether a facility could, because of its location, reasonably be expected to cause significant and substantial harm to the environment by discharging oil into or on the navigable waters or adjoining shorelines, the Regional Administrator may consider the factors in paragraph (f)(2) (SLIDE 35) of this section as well as the following:
  (i) Frequency of past discharges;
  (ii) Proximity to navigable waters;
  (iii) Age of oil storage tanks; and
  Vulnerable Receptors will be impacted prior to arrival and deployment of response assets
  (iv) Other facility-specific and Region-specific information, including local impacts on public health.
EPA will issue notification of determination
The Regional Administrator shall review plans submitted by such facilities EVERY 5 YEARS

## Slide 39: Submissions & Amendments
Prior to start of new operations
  60 days for amendments
Newly subject to 112.20(f)(1)
  6 months
60 days after material changes
1,000,000 Gallons X Oil
1,999,990 Gallons Y Oil
112.20(a)(2)(ii)-(iv), 112.20(d)(1),112.20(d)(2)
Notes: 40 CFR 112. 20 also states that facilities must revise AND resubmit the revised plan within 60 days of each change that materially may affect the response to a worst case discharge, including:
A change in the facility’s configuration
A change in the type of oil handled, stored, or transferred;
• A change in capabilities of any oil spill removal organization that provides equipment and personnel to respond to oil discharges from the facility; or
• A change in the facility’s discharge prevention and response equipment or emergency response procedures.

## Slide 40: General Requirements
Contents and Format
Follow appendix F format or use a cross-reference for ICP
Emergency Response Action Plan
FRP Contents described 112.20(h)1-11
Field Actions
Spill response training program
Drills and exercise program
Operable and ready equipment
Consistent with the NCP and Area Contingency Plans
Notes: The FRP should:
Follow appendix F format or use a cross-reference for ICP
Include an Emergency Response Action Plan
FRP Contents described 112.20(h)1-11 See Module 4
Field Actions:
Spill response training program
Drills and exercise program
Operable and ready equipment
Consistent with the NCP and Area Contingency Plans

## Slide 41: Recap-SPCC and FRP Rules
Facility Response Plan
SPCC

## Slide 42: Recap-SPCC Plan Preparation and Amendments
  SPCC Plan must be certified by a Professional Engineer (PE)
  A PE must certify any technical amendments
  SPCC Plan must have the full approval of management
  A plan should be amended and resubmitted in the case of any material changes at the facility
  SPCC plans should be reviewed and resubmitted every five years.
Notes:   SPCC Plan must be certified by a PE
  A Professional Engineer must certify any technical amendments
  SPCC Plan must have the full approval of management
  A plan should be amended and resubmitted in the case of any material changes at the facility
  SPCC plans should be reviewed and resubmitted every five years.

## Slide 43: Recap – FRP
Facilities who are subject to the FRP Rule required to prepare an FRP
FRP Harm Categories
  A facility may be determined to pose substantial harm.
  A facility may be designated as posing significant‑and‑substantial harm.
The purpose of the FRP rule is to ensure facilities have an approved FRP to respond to the Worst-case discharge
Notes: FRP Harm Categories
  A facility may be determined to pose substantial harm.
  A facility may be designated as posing significant‑and‑substantial harm.

## Slide 44: FRP Submissions:
  FRP/ERAP
  FRP review every 5 years
Facility should conduct amendments:
If required by Regional Administrator
If there is a Material change
After a 5-year review if there is a material change
Facility Response Plan
Notes: 45. FRP Submissions: includes:
  FRP/ERAP
  FRP review every 5 years
Facility should conduct amendments:
If required by Regional Administrator
If there is a Material change
After a 5-year review if there is a material change

## Slide 45
      QUESTIONS?