## Slide 1: SPCC/FRP Inspection Process
Notes: In this module, we will cover the SPCC/FRP inspection process:
Let’s start by discussing: How do we target facilities for inspection?
Higher‑risk sites (large marine terminals, FRP)
  Spill history
Sectors with known noncompliance
Partner referrals
Citizen complaints

## Slide 2: Records Reviews
Verify SPCC/FRP/ERAP is available to response personnel
Equipment Inspection Logs
Drainage logs
Discharge Prevention Meeting Logs
Drill, exercise and equipment deployment logs
Integrity testing (API 653, STI SP001)
Training records
PREP program implementation
Notes: Inspectors will ask to see the onsite copy of the SPCC, FRP, and ERAP
Copies of most current records of the facility as required by the SPCC/FRP rules
Include discussion of handout listing required records
Records:
Tank, piping, valves, secondary containment inspections
Equipment Inspection Logs
Drainage logs
Discharge Prevention Meeting Logs
Integrity testing records
Training records
Documentation of PREP program implementation, including:
QI Notification exercise
Tabletop exercises
Facility and/or OSRO equipment deployment exercises

## Slide 3: Field Inspection
Verify plan accuracy
Secondary containment adequacy (Appendix F 1.8.1.3)
Facility components are in good working order
Hazard evaluation and vulnerability analysis accurate
Facility diagrams are accurate
Notes: Field Inspection –
The INSPECTOR will ask to walk around the facility to verify the accuracy of the FRP and
observe the condition and adequacy of oil storage tanks and containers, piping, secondary containment, and
Of course, to verify that facility components are in good working order
We will verify the accuracy of
Hazard evaluation and vulnerability analysis
Facility diagrams
.

## Slide 4: Response Equipment (Appendix F 1.8.1.2)
Verify equipment listed in plan is accurate
Verify testing/deployment records are accurate and up to date
If fully OSRO dependent, how do you ensure OSRO knows where to deploy and with what equipment?
Notes: The inspector will also want to see facility response equipment during the walkaround to evaluate its condition, and accuracy of description in the FRP.
We want to verify:
Location
Year of purchase
Containment capacities
Pumping capacity (gal/hr). Etc.
Verify testing/deployment records are accurate and up to date
If fully OSRO dependent, how do you ensure OSRO knows where to deploy and with what equipment?

## Slide 5: Common Observations
Leaks from valves and connection points
Improperly braced or supported piping
Discrepancies with diagrams and facility layout (piping and drainages)
Missing inspection documentation
Out of date notification lists
Notes: Is a facility required to clean up discharged oil wholly contained within a diked area? YES
Requirements to clean up discharged oil
Non-production
40 CFR 112.8(c)(10): Promptly correct visible discharges which result in a loss of oil from the container, including but not limited to seams, gaskets, piping, pumps, valves, rivets, and bolts. You must promptly remove any accumulations of oil in diked areas.
Other common observations:
Leaks from valves and connection points
Improperly braced or supported piping
Discrepancies with diagrams and facility layout (piping and drainages)
Missing inspection documentation
Out of date notification lists
Production
40 CFR 112.9(b)(2): Inspect at regularly scheduled intervals field drainage systems (such as drainage ditches or road ditches), and oil traps, sumps, or skimmers, for an accumulation of oil that may have resulted from any small discharge. You must promptly remove any accumulations of oil.
40 CFR 112.9(c)(5)(iii): Promptly remove or initiate actions to stabilize and remediate any accumulations of oil discharges associated with flow-through process vessels.
40 CFR 112.9(c)(6)(iv): Promptly remove or initiate actions to stabilize and remediate any accumulations of oil discharges associated with the produced water container.
40 CFR 112.9(d)(4)(iv): Promptly remove or initiate actions to stabilize and remediate any accumulations of oil discharges associated with flowlines, intra-facility gathering lines, and associated appurtenances.
What are the minimum requirements for training oil-handling personnel?
40 CFR 112.7(f)(1): At a minimum, train your oil-handling personnel in the operation and maintenance of equipment to prevent discharges; discharge procedure protocols; applicable pollution control laws, rules, and regulations; general facility operations; and, the contents of the facility SPCC Plan.
How often should discharge prevention briefings be held?
40 CFR 112.7(f)(3): Schedule and conduct discharge prevention briefings for your oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan for that facility. Such briefings must highlight and describe known discharges as described in § 112.1(b) or failures, malfunctioning components, and any recently developed precautionary measures.
Do you have to include exempted pipe lines on facility diagrams? YES
40 CFR 112.7(a)(3): The facility diagram must identify the location of and mark as “exempt” underground tanks that are otherwise exempted from the requirements of this part under § 112.1(d)(4). The facility diagram must also include all transfer stations and connecting pipes, including intra-facility gathering lines that are otherwise exempted from the requirements of this part under § 112.1(d)(11).

## Slide 6: Post-Inspection/Drill Follow Up
The inspector will debrief with the QI, facility personnel, and/or OSROs
The facility will receive a letter documenting the inspections/drill including any findings and recommendations.
45 days from time of notice to apply recommendations
Notes: The facility will receive signed Notice of the inspection and/or drill on the same day

## Slide 7: Recap
Records Reviews:
  FRP/ERAP/SPCC
  Inspection records, Exercise Logs, (Printout/electronic link)
Field Inspection (Response Equipment/Facility walk through/layout verification)
Post-Inspection Exit Meeting
Post-Inspection/Drill Letter
Notes: 7. We will Conduct Records review:
To verify the availability of the FRP/ERAP/SPCC
We will ask for most current records of facility as required by the FRP/SPCC rule
During the Field Inspection:
Post-Inspection/Drill Follow Up
Post-Inspection Exit Meeting
Post-Inspection/Drill Letter

## Slide 8: Bonus: FRP Review and Approval Process
Plan submittal
  Requested, or revised FRP received
Technical review
Deficiency notice
Facility correction window
  45 days to address deficiencies and resubmit (or as specified in the notice).
Follow‑up review
  EPA reviews the revised FRP; additional clarifications requested if needed.
Issue approval letter

## Slide 9
      QUESTIONS?